## Energy and Roofing
| Owner & Facility |  |  | Energy Usage Data |  | Solar Project Info | [9 empty] | Roofing Information |  |  | Additional Notes
| Owner | Facility Name | Street Address | 12 Mo. kWh Usage (kWh) | 12 Mo. High Peak Demand (kW) | DC Capacity (kWdc) | AC Capacity (kWac) | Annual Output (KWH) | Facility Usage Offset by Solar | PV Module wattage | PV module Qty | String Sizing | Inverter - MFR / Model | Inverter - Capacity (kW) | Inverter - Quantity | Roof Material | Roof Warranty | Roof Manufacturer | Notes
Group A | Buncombe County | West Asheville Library | 942 Haywood Rd. Asheville, NC | 49640 | 24 | 30.03 | 22.8 | 42331 | 85.28% | 385 | 78 | 3s x 13m | SolarEdge SE11400H-US | 11.4 | 2 | Replacing with TPO in 2020 | There will be a weatherization warranty on the new roof | TBD | Small local library - Getting new roof in 2020
| Buncombe County | South Buncombe Library | 260 Overlook Rd. Asheville, NC | 76800 | 31 | 36.96 | 28.8 | 43291 | 56.37% | 385 | 96 | 1s x 16m, 2s x 17m & 2s x 15m, 1s x 16 | SolarEdge SE14.4kUS | 14.4 | 2 | Asphalt Shingle | No Warranty is in place | Unknown | Small local library
| Buncombe County | Tax Office | 94 Coxe Ave. Asheville, NC | 148920 | 59 | 36.96 | 28.8 | 51962 | 34.89% | 385 | 96 | 3s x 16m | SolarEdge SE14.4kUS | 14.4 | 2 | Replacing with TPO in 2020 | There will be a weatherization warranty on the new roof | TBD | Getting new roof in 2020
| Buncombe County | Health and Human Services Building - Parking Deck | 40 Coxe Ave. Asheville, NC | 1645920 | 371 | 242.55 | 183.3 | 326128 | 19.81% | 385 | 630 | 10s x 18m (50kW) 5s x 18m (33.3kW) | SMA STP 50-US-41 SMA STP 33-US-41 | 50 & 33.3 | 50 x 3, 33.3 x 1 | N/A - Parking Deck | N/A - Parking Deck | N/A - Parking Deck | Canopies on top deck level of parking deck
| Buncombe County | College St. Parking Deck - House Loads | 164 College St. Asheville, NC | 261700 | 54 | 69.3 | 50 | 92065 | 35.18% | 385 | 180 | 10s x 18m | SMA STP 50-US-41 | 50 | 1 | N/A - Parking Deck | N/A - Parking Deck | N/A - Parking Deck | Canopies on top deck level of parking deck - serving house loads
| Buncombe County | College St. Parking Deck - Family Justice Cntr Loads | 164 College St. Asheville, NC | 918500 | 430 | 173.25 | 133.3 | 229117 | 24.94% | 385 | 450 | 10s x 18m (50kW) 5s x 18m (33.3kW) | SMA STP 50-US-41 SMA STP 33-US-41 | 50 & 33.3 | 50 x 2, 33.3 x 1 | N/A - Parking Deck | N/A - Parking Deck | N/A - Parking Deck | Canopies on top deck level of parking deck - serving Family Justice Center loads at 35 Woodfin Pl
| Buncombe County | Fairview Library | 1 Taylor Rd. Fairview, NC | 68118 | 46 | 36.19 | 28.8 | 43409 | 63.73% | 385 | 94 | 2s x 16m, 1s x 15m (each) | SolarEdge SE14.4kUS | 14.4 | 2 | Metal Standing Seam | No Warranty is in place | Unknown | Small public library
| Buncombe County | Leicester Library | 1561 Alexander Rd. Leicester, NC | 74800 | 46 | 33.495 | 26.6 | 49507 | 66.19% | 385 | 87 | 1s x 12m, 1s x 13m (7.6) 2s x 12m, 1s x 13 (11.4) | SolarEdge SE11400H-US SolarEdge SE7600H-US | 11.4 & 7.6 | 11.4 x 1, 7.6 x 2 | Metal Standing Seam | No Warranty is in place | Unknown | Small public library
| Buncombe County | North Asheville Library | 1030 Merrimon Ave. Asheville, NC | 38109 | 24 | 32.34 | 23.4 | 36809 | 96.59% | 385 | 84 | 2s x 16m (9kW) 2s x 17m, 1s x 18m (14.4) | SolarEdge SE14.4kUS SolarEdge SE9kUS | 14.4 & 9 | 14.4 x 1, 9 x 1 | Asphalt Shingle | No Warranty is in place | Unknown | Small public library
| Buncombe County | Transfer Station | 220 Hominy Creek Rd. Asheville, NC | 168600 | 83 | 107.8 | 80 | 138698 | 82.26% | 385 | 280 | 2s x 35m (20kW) 3s x 35m (30kW) | SolarEdge SE30kUS SolarEdge SE20kUS | 30 & 20 | 30 x 2, 20 x 1 | Corrugated Metal (Ribbed) | There is a material warranty on this roof but no weatherization warranty is in place. | A&S | Roof installed in 2018
| Buncombe County | Animal Shelter | 16 Forever Friend Ln. Asheville, NC | 644798 | 143 | 186.725 | 139.9 | 244512 | 37.92% | 385 | 485 | 2s x 35m (20kW) 2s x 38m, 1s x 39m (33.3) | SolarEdge SE33.3kUS SolarEdge SE20kUS | 33.3 & 20 | 33.3 x 3, 20 x 2 | Metal Standing Seam | No Warranty is in place | Unknown | Roof is 10 years old
| Buncombe County | Old Firemans Training Center | 180 Erwin Hills RD. Asheville, NC | 57872 | 23 | 30.03 | 22.8 | 40336 | 69.7% | 385 | 78 | 3s x 13m | SolarEdge SE11400H-US | 11.4 | 2 | Asphalt Shingle | No Warranty is in place | Unknown | Roof is 2-3 Years old
| Buncombe County | Buncombe PSTC - Training Center | 20 Canoe Ln. Woodfin, NC | 348640 | 129 | 133.21 | 99.9 | 186782 | 53.57% | 385 | 346 | 1x (3s x 38m,) 2x (1s x 38m, 2s x 39m) | SolarEdge SE33.3kUS | 33.3 | 3 | TPO | The roof has a weatherization warranty | Johns Manville | TPO Roof is 3-4 YRS
| Buncombe County | Buncombe PSTC - Apparatus Center | 1 Canoe Ln. Woodfin, NC | 125760 | 59.2 | 70.07 | 53.3 | 94827 | 75.4% | 385 | 182 | 2s x 35m (20kW) 2s x 37m, 1s x 38m (33.3) | SolarEdge SE33.3kUS SolarEdge SE20kUS | 33.3 & 20 | 33.3 x 1, 20 x 1 | Metal Standing Seam and TPO | The TPO roof has a weatherization warranty. The metal roof has a material warranty and no weatherization warranty. | Metal Roofing Systems (Metal) and Johns Manville (TPO) | Roof is 3-4 Years Old
| City Of Asheville | Burton Street Community Center | 134 Burton Street Asheville, NC | 65000 | 58 | 40.81 | 30 | 54894 | 84.45% | 385 | 106 | 2x (3s x 12m) 1x (2s x 11m, 1s x 12m) | SolarEdge SE10000H-US | 10 | 3 | Asphalt Shingle | No Warranty is in place | Unknown | Community Center - Roof is 10 years old
| City Of Asheville | Linwood Crump Shiloh Center | 121 Shiloh Rd Asheville, NC | 130440 | 36 | 47.74 | 36 | 67308 | 51.6% | 385 | 124 | 1s x 15m, 1s x 16m | SolarEdge SE9kUS | 9 | 4 | TPO | The roof has a weatherization warranty | Johns Manville | Community Center - Roof is one year old
| City Of Asheville | Wall Street Parking Deck - House Loads | 45 Wall Street Asheville, NC | 97680 | 34 | 43.505 | 34 | 56903.7 | 58.26% | 385 | 113 | 4s x 10m (12kW) 3s x 11m (10kW) | Fronius SYMO 12.0-3 208 Fronius SYMO 10.0-3 208 | 12 & 10 | 12 x 2, 10 x 1 | N/A - Parking Deck | N/A - Parking Deck | N/A - Parking Deck | Canopies - For House Loads Account
| City Of Asheville | Wall Street Parking Deck - Parking Sevices | 45 Wall Street Asheville, NC | 50007 | 29 | 30.8 | 24 | 40643.4 | 81.28% | 385 | 80 | 4s x 10m | Fronius SYMO 12.0-3 208 | 12 | 2 | N/A - Parking Deck | N/A - Parking Deck | N/A - Parking Deck | Canopies - For Parking Sevices Account
| City Of Asheville | Wall St. Parking Deck - Sell All System | 45 Wall Street Asheville, NC | N/A | N/A | 63.525 | 50 | 82936 | N/A - Sell- All | 385 | 165 | 3s x 11m | Fronius SYMO 10.0-3 208 | 10 | 5 | N/A - Parking Deck | N/A - Parking Deck | N/A - Parking Deck | Canopies - Sell- All System
| City Of Asheville | Fire Station #10 | 1903 Old Haywood Rd. Asheville, NC | 108800 | 26 | 31.185 | 23.4 | 41312 | 37.97% | 385 | 81 | 1s x 15m, 1s x 16m (9kW) 1s x 16m, 2s x 17m (14.4) | SolarEdge SE14.4kUS SolarEdge SE9kUS | 14.4 & 9 | 14.4 x 1, 9 x 1 | Metal Standing Seam | No Warranty is in place | Unknown | Fire Station - Roof installed in 07'
| City Of Asheville | Fire Station #11 | 7 Rocky Ridge Rd. Asheville, NC | 98238 | 25 | 30.8 | 23.4 | 43174 | 43.95% | 385 | 80 | 2s x 15m (9kW) 1s x 16m, 2s x 17m (14.4) | SolarEdge SE14.4kUS SolarEdge SE9kUS | 14.4 & 9 | 14.4 x 1, 9 x 1 | Metal Standing Seam | No Warranty is in place | Unknown | Fire Station - Roof installed in 08'
Group B | AB TECH | Asheville Campus - Allied Health | 10 Genevieve Circle Asheville, NC | 1713120 | 609 | 107.415 | 80 | 138397 | 8.079% | 385 | 279 | 1x (1s x 34m, 1s x 35m) 3x (2s x 35m) | SolarEdge SE20kUS | 20 | 4 | Standing Seam Metal | The roof has a weatherization warranty. | McElroy Metals | Roof is two years old
| AB TECH | Asheville Campus - Bailey | 340 Victoria Rd. Asheville, NC | 394048 | 165 | 115.5 | 86.4 | 159676 | 40.52% | 385 | 300 | (1s x 16m, 2s x 17m) | SolarEdge 14.4kUS | 14.4 | 6 | TPO | The roof has a weatherization warranty | Firestone | Roof is ten years old
| AB TECH | Asheville Campus - Birch | 17 Student Circle Asheville, NC | 311800 | 130 | 115.5 | 86.4 | 155206 | 49.78% | 385 | 300 | (1s x 16m, 2s x 17m) | SolarEdge 14.4kUS | 14.4 | 6 | TPO | The roof has a weatherization warranty | Unknown | Roof is 4 years old
| AB TECH | Asheville Campus - Conference Center | 16 Fernihurst. Asheville, NC | 313760 | 98 | 117.04 | 86.6 | 164579 | 52.45% | 385 | 304 | (1s x 34m, 1s x 36m) (20kW) 3s x 39m (33.3kW) | SolarEdge SE20kUS SolarEdge SE 33kUS | 20 & 33.3 | 20 x 1, 33.3 x 2 | TPO | The roof has a weatherization warranty | Unknown | Roof is 4 years old
| AB TECH | Asheville Campus - Coman/Locke | 10 Fernihurst Dr. Asheville, NC | 1597500 | 498 | 135.905 | 115.2 | 187431 | 11.73% | 385 | 353 | 1x (2s x 14m, 1s x 15m) 4x (2s x 15m, 1s x 14m)- Coman, 1x (1s x 14m, 2s x 15m) 2x (3s x 15m) - Locke | SolarEdge 14.4kUS | 14.4 | 8 | Asphalt Shingle & TPO | The roof has a weatherization warranty | Johns Manville - Coman/ Locke - Carlisle | Roof is 2 years old
| AB TECH | Asheville Campus - Ferguson | 19 Tech Dr. Asheville, NC | 280300 | 92 | 105.875 | 80 | 146168 | 52.15% | 385 | 275 | 1x (2s x 34m) (20kW) 3x (1s x 34m, 1s x 35m) (20kW) | SolarEdge SE20kUS | 20 | 4 x 20 | TPO | The roof has a weatherization warranty | Johns Manville | Roof is 3 years old
| AB TECH | Asheville Campus - Hemlock | 207 Victoria Rd. Asheville, NC | 529100 | 168 | 92.4 | 80 | 133564 | 25.24% | 385 | 240 | 2s x 30m | SolarEdge SE20kUS | 20 | 4 | TPO | The roof has a weatherization warranty | Johns Manville | Roof is 3 years old
| Asheville City Schools | Hall Fletcher Elementary School | 60 Ridgelawn Rd. Asheville, NC | 578200 | 206.4 | 257.18 | 199.8 | 363106 | 62.8% | 385 | 668 | 2x (2s x 37m, 1s x 38m) 4x (3s x 37m) | SolarEdge SE 33kUS | 33.3 | 6 | Bitumen | No Warranty is in place | Unknown | Roof is a few years old
| Asheville City Schools | Vance Elementary School | 98 Sulpher Springs Rd. Asheville, NC | 370200 | 198.4 | 256.025 | 193.2 | 363878 | 98.29% | 385 | 665 | 3x (2s x 34m) (20kW) 3x (2s x 38m, 1s x 39m) (33.3kW) 1x (1s x 38m, 2s x 39m) (33.3kW) | SolarEdge SE20kUS SolarEdge SE33.3kUS | 20 & 33.3 | 20 x 3 33.3 x 4 | Built-Up with pebble ballast | No Warranty is in place | Unknown | Roof is 10 years old but in great condition
| Asheville City Schools | Montford Northstar Academy | 90 Montford Ave. Asheville, NC | 337440 | 148 | 187.88 | 139.9 | 257654 | 76.36% | 385 | 488 | 2x (2s x 35m) (20kW) 3x (1s x 38m, 2s x 39m) (33.3kW) | SolarEdge SE20kUS SolarEdge SE33.3kUS | 20 & 33.3 | 20 x 2 33.3 x 3 | TPO | The roof has a weatherization warranty | Unknown | Roof is 3 years old
| Asheville City Schools | Asheville Middle School | 211 S. French Broad St. Asheville, NC | 1618000 | 503.2 | 363.44 | 299.7 | 499182 | 30.85% | 385 | 944 | 1x (1s x 34m, 2s x 35m) 8x (3s x 35m) | SolarEdge SE 33kUS | 33.3 | 9 | TPO | The roof has a weatherization warranty | Soprema | Roof is 4 years old
| Asheville City Schools | Ira B Jones Elementary School - Large Account | 544 Kimberly Ave. Asheville, NC | 332480 | 164.8 | 209.44 | 159.9 | 266427 | 80.13% | 385 | 544 | 3x (2s x 34m) (20kW) 1x (2s x 37m, 1s x 38m) (33.3kW) 2x (3s x 38m) (33.3kW) | SolarEdge SE20kUS SolarEdge SE33.3kUS | 20 & 33.3 | 20 x 3 33.3 x 3 | Asphalt Shingle & TPO | The TPO roof has a weatherization warranty. The shingle roof has no warranty. | Unknown | Roof is 3 years old
| Asheville City Schools | Ira B Jones Elementary School - Small Account | 544 Kimberly Ave. Asheville, NC | 140900 | 54 | 69.3 | 53.3 | 96473 | 68.47% | 385 | 180 | (2s x 34m) (20kW) (2s x 37m, 1s x 38m) (33.3kW) | SolarEdge SE20kUS SolarEdge SE33kUS | 21 & 33.3 | 20 x 1 33.3 x 1 | Asphalt Shingle & TPO | The TPO roof has a weatherization warranty. The shingle roof has no warranty. | Unknown | Roof is 3 years old
| Asheville City Schools | Asheville High School - Vocational Building | 419 McDowell St. Asheville, NC | 571800 | 138 | 178.64 | 133.2 | 247608 | 43.3% | 385 | 464 | (1s x 38m, 2s x 39m) | SolarEdge SE33kUS | 33.3 | 4 | TPO | The roof has a weatherization warranty | Unknown | Roof is 3 years old
| Asheville City Schools | Asheville High School - Cafeteria | 419 McDowell St. Asheville, NC | 284400 | 108 | 118.58 | 99.9 | 160974 | 56.6% | 385 | 308 | 1x ( 3s x 34m) 2x (2s x 34m, 1s x 35m) | SolarEdge SE33kUS | 33.3 | 3 | Standing Seam Metal | No Warranty is in place | Unknown | Roof approx 15 years old
| Asheville City Schools | Asheville High School - Cultural Arts Building | 419 McDowell St. Asheville, NC | 252100 | 123 | 112.035 | 95.4 | 141539 | 56.14% | 385 | 291 | 1x (1s x 13m, 1s x 14m) (9kW) 6x (1s x 14m, 2s x 15m) (14.4kW) | SolarEdge 14.4kUS SolarEdge 9kUS | 9 & 14.4 | 9 x 1 14.4 x 6 | Standing Seam Metal | No Warranty is in place | Unknown | Roof approx 15 years old
| Buncombe Co. Schools | Hominy Valley Elementary School | 450 Enka Lake Rd. Asheville, NC | 533200 | 320 | 304.92 | 250 | 451937 | 84.76% | 385 | 792 | 1x (8s x 18m) 4x (9s x 18m) | SMA STP Core 62_US_41 | 62.5 | 4 | N/A - Ground-Mount | N/A - Ground-Mount | N/A - Ground-Mount | Ground-Mount for Elementary School
| Buncombe Co. Schools | Enka Intermediate School | 125 Asheville Commerce Pkwy. Asheville, NC | 745270 | 393 | 439.285 | 366.3 | 637984 | 85.6% | 385 | 1141 | Roof - 1x (1s x 35m, 2s x 36m) 3x (3s x 36m) Ground - 1x (3s x 33m) 1x (1s x 33, 2s x 34m) 5x (3s x 34m) | SolarEdge SE33.3kUS | 33.3 | 11 | Standing Seam Metal | The roof has a weatherization and paint warranty. | MRS | Ground-Mount and Roof-Mount for Elementary School - Roof is 3 years old
| Buncombe Co. Schools | Glen Arden Elementary School | 50 Pinehurst Circle, Arden, NC | 486400 | 324 | 256.41 | 200 | 387779 | 79.72% | 385 | 666 | 1x (10s x 18m) 3x (9s x 18m) | SMA STPCore 50_US_41 | 50 | 4 | N/A - Ground-Mount | N/A - Ground-Mount | N/A - Ground-Mount | Elementary School - Roof is 10 years old
| Buncombe Co. Schools | Community High School | 235 Old US HWY 70, Swannanoa, NC | 347220 | 165 | 207.9 | 145.5 | 291926 | 84.08% | 385 | 540 | (7s x 18m) (33kW) (10s x 18m) (50kW) (13s x 18m) (62.5kW) | SMA STPCore 33_US_41 SMA STP Core 50_US_41 SMA STP Core 62_US_41 | 33, 50 & 62.5 | 33 x 1 50 x 1 62.5 x 1 | N/A - Ground-Mount | N/A - Ground-Mount | N/A - Ground-Mount | Ground-Mount for Elementary School - Utility data is only a few months old and 12 month usage data has been extrapolated to estimate the solar capacity. System size may be subject to increase or decrease based on energy usage profile over the next 6-9 months.
| Buncombe Co. Schools | Cane Creek Middle School | 570 Lower Brush Creek Rd. Fletcher, NC | 689250 | 397 | 388.08 | 312.5 | 586789 | 85.13% | 385 | 1008 | 1x (12s x 18m) 4x (11s x 18m) | SMA STP Core 62_US_41 | 62.5 | 5 | N/A - Ground-Mount | N/A - Ground-Mount | N/A - Ground-Mount | Ground-Mount for Middle School
| Buncombe Co. Schools | North Windy Ridge Intermediate School | 20 Doan Rd. Weaverville, NC | 631400 | 418 | 365.365 | 299.7 | 477633 | 75.65% | 385 | 949 | 7x (3s x 35m) 2x (1s x 35m, 2s x 36m) | SolarEdge SE33kUS | 33.3 | 9 | Standing Seam Metal | The roof has a weatherization and paint warranty. | MBCI | Intermediate School - Roof is 10 years old
| Buncombe Co. Schools | Buncombe Aquatic Center | 18 Ensley Stadium Loop, Asheville, NC | 798240 | 157 | 207.9 | 150 | 304692 | 38.17% | 385 | 540 | 10s x 18m | SMA STP Core 50_US_41 | 50 | 3 | N/A - Ground-Mount | N/A - Ground-Mount | N/A - Ground-Mount | Ground Mount for new aquatic facility
| Buncombe Co. Schools | Erwin High - Kitchen Account | 60 Lees Creek Rd. Asheville, NC | 700000 | 333 | 381.15 | 312.5 | 554569 | 79.22% | 385 | 990 | 11s x 18m | SMA STP Core 62_US_41 | 62.5 | 5 | N/A - Ground-Mount | N/A - Ground-Mount | N/A - Ground-Mount | Ground-Mount for High School - Kitchen Account
| Buncombe Co. Schools | Erwin High - Main Account | 60 Lees Creek Rd. Asheville, NC | 429200 | 252 | 207.9 | 150 | 294386 | 68.59% | 385 | 540 | 10s x 18m | SMA STP Core 50_US_41 | 50 | 3 | N/A - Ground-Mount | N/A - Ground-Mount | N/A - Ground-Mount | Ground-Mount for High School - Main Account
| Buncombe Co. Schools | Owen Middle School | 739 Old US HWY 70, Swannanoa, NC | 449920 | 188 | 249.095 | 186.5 | 309892 | 68.88% | 385 | 647 | (1s x 34m, 1s x 36m) - (20kW) 3x (2s x 38m, 1s x 39m) 2x (1s x 38m, 2s x 39m) - (33.3kW) | SolarEdge SE20kUS SolarEdge SE33.3kUS | 20 & 33.3 | 20 x 1 33.3 x 5 | Standing Seam Metal | The roof has a weatherization and paint warranty. | MBCI | Roof is 3 years old
| Total |  |  | 20613590 | 8081 | 7057.435 | 5504.4 | 9786394.1 | 47.48%